## Objects
KERMI KNX-RVU Interface v 2.0 - 2019-09-23
KNX CO data
CO Index | KNX DPT | KNX Flags | CYC | Var name | Description
0 | 7.Model | CR-T- |  | CtrlModel | Controller model
1 | 7.FWRel | CR-T- |  | FW_Release | Firmware Release
2 | 7.FWRel | CR-T- |  | TEP_FW_Release | T-EP Firmware Release
3 | 9.001 | CR-T- | X | TempProbe1 | Probe 1 temperature
4 | 9.001 | CR-T- | X | TempProbe2 | Probe 2 temperature
5 | 9.001 | CR-T- | X | TempProbe3 | Probe 3 temperature
6 | 9.001 | CR-T- | X | TempProbe4 | Probe 4 temperature
7 | 1.011 | CR-T- | X | STM_RemoteOff | Remote OFF active
8 | 1.011 | CR-T- | X | STM_Bypass | Bypass active
9 | 1.011 | CR-T- | X | STM_ElecPreHeat | Electric Pre Heater active
10 | 1.011 | CR-T- | X | STM_WaterPreHeat | Water pre-heating active
11 | 1.011 | CR-T- | X | STM_Boost | Boost active
12 | 1.011 | CR-T- | X | STM_DefrostCycle | Defrost cycle active
13 | 1.011 | CR-T- | X | STM_PartyMode | Party Mode active
14 | 1.011 | CR-T- | X | STM_StateOn | On status
15 | 1.002 | CR-T- | X | STM_Winter | not used
16 | 9.007 | CR-T- | X | HumiditySet | Humidity setpoint
17 | 7.007 | CR-T- | X | FilterCounter | Filter counter
18 | 1.011 | CR-T- | X | DIN_C1 | Input C1 status
19 | 1.011 | CR-T- | X | DIN_C2 | Input C2 status
20 | 1.011 | CR-T- | X | DIN_C3 | Input C3 status
21 | 1.011 | CR-T- | X | DIN_C4 | not used
22 | 1.005 | CR-T- | X | ALM_General | General Alarm
23 | 1.005 | CR-T- | X | ALM_T1_Fail | T1 probe failure alarm
24 | 1.005 | CR-T- | X | ALM_T2_Fail | T2 probe failure alarm
25 | 1.005 | CR-T- | X | ALM_T3_Fail | T3 probe failure alarm
26 | 1.005 | CR-T- | X | ALM_T4_Fail | T4 probe failure alarm
27 | 1.005 | CR-T- | X | ALM_Timekeeper | Timekeeper failure alarm
28 | 1.005 | CR-T- | X | ALM_Frost | Frost alarm
29 | 1.005 | CR-T- | X | ALM_Frost_T2 | Frost alarm (from T2 probe)
30 | 1.005 | CR-T- | X | ALM_Fireplace | Fireplace Alarm
31 | 1.005 | CR-T- | X | ALM_PressTxFail | Pressure transducer failure alarm
32 | 1.005 | CR-T- | X | ALM_Filter | Filter alarm
33 | 1.005 | CR-T- | X | ALM_FansFail | Fans failure
34 | 1.005 | CR-T- | X | ALM_RH_CO2_TxFail | RH or CO2 sensor failure alarm
35 | 1.005 | CR-T- | X | ALM_FanThermalInput | Fan thermic input alarm
36 | 1.005 | CR-T- | X | ALM_PreHeating | Pre Heating alarm
37 | 1.005 | CR-T- | X | ALM_PreFrost_T2 | Pre frost alarm (T2)
38 | 9.008 | CR-T- | X | CO2Value | CO2 reading
39 | 9.007 | CR-T- | X | RelHumValue | RH reading
40 | 1.002 | CR-T- |  | OPT_IAQ | IAQ Used
41 | 1.002 | CR-T- |  | OPT_PostTreatment | Post treatment used
42 | 1.002 | CR-T- |  | OPT_HE | HE used
43 | 1.002 | CR-T- |  | OPT_BoilerBoost | not used
44 | 1.002 | CR-T- |  | OPT_CO2Sensor | CO2 sensor present
45 | 1.002 | CR-T- |  | OPT_DiffPressSensor | Differential pressure sensor present
46 | 1.002 | CR-T- |  | OPT_RHSensor | RH sensor present
47 | 1.002 | CR-T- |  | OPT_ReverseMount | Reverse mounting
48 | 5.SpdSel | C-W-U |  | ManSpeedNrSet | Manual Speed command
49 | 5.SpdSel | CR-T- | X | ManSpeedNrActual | Manual Speed status
50 | 1.001 | C-W-U |  | CMD_OnOff | On/Off Command
51 | 1.011 | CR-T- | X | S_CMD_OnOff | On/Off status
52 | 1.001 | C-W-U |  | CMD_Manual | Manual mode command
53 | 1.011 | CR-T- | X | S_CMD_Manual | Manual mode status
54 | 1.001 | C-W-U |  | CMD_Holiday | Holiday mode command
55 | 1.011 | CR-T- | X | S_CMD_Holiday | Holiday mode status
56 | 1.001 | C-W-U |  | CMD_Party | Party mode command
57 | 1.011 | CR-T- | X | S_CMD_Party | Party mode status
58 | 1.001 | C-W-U |  | CMD_Auto | Auto mode command
59 | 1.011 | CR-T- | X | S_CMD_Auto | Auto mode status
60 | 10.001 | CRWTU |  | Time_Day | Time